April 18, 2020

UCLA Capital Programs

Standard Specification for Sternberg Acorn Lamp Fixture

NEW LED STERNBERG ACORN LAMP FIXTURE

Avenue Series B750-VCOB – Fixture shall have a textured acrylic acorn lens with a perforated brass decorative ring and a top finial with a Dark Bronze Smooth finish.

Fixture shall have the VCOB Led module with a 4000K color temperature and a minimum 70 CRI or better with a Symmetric and Asymmetric distribution options. LED shall offer a minimum life of 100,000 hours at L70. Fixture shall have a wattage of 56 and lumens per watt shall be 111 or better.

Fixture driver shall be high efficiency with a THD less than 20% and a high-power factor greater than .9 and be capable of a 0-10v signal.

Fixture manufacturer shall offer a seven-year limited warranty.

Acorn shall mount on a historic fluted and flared fitter. Fitter shall offer the TL (Twist-Lock) fitter shall have an aluminum die-cast twist-lock mechanism. The tool-less ¼ turn action allows for easy globe removal and replacement. A die-cast ring assembly is mechanically attached to the globe and is removable if the globe is broken or replaced.

Pole shall be 6200 Oxford Series and a standard height of 12ft. Pole shall be a cast tapered fluted pole with a one-piece decorative heavy wall 356 alloy cast aluminum base.

Fixture and pole shall be painted a Dark Bronze Smooth finish.

ORDER NUMBER:

SYMMETRIC OPTIC – (Light source distributes light evenly in all directions)

STERNBERG – PT-B750-5T-VCOB-4L-40-TS-MDL03-A-PBDR—GFF DB-DB-6212-TFP63-DB

ASYMMETRIC OPTIC – (Light source distributes light to one side)

STERNBERG – PT-B750-5T-VCOB-4L-40-TA-MDL03-A-PBDR—GFF DB-DB-6212-TFP63-DB

LED CONVERSION KIT FOR B750 AVENUE SERIES ACORN

ORDER NUMBER:

SYMMETRIC DISTRIBITION – LIGHT SOURCE DISTRIBUTES LIGHT EVENLY IN ALL DIRECTIONS

VCOB-B750-4L-40-TS-MDL03-682/682M

ASYMMETRIC – LIGHT SOURCE DISTRIBUTES LIGHT TO ONE SIDE

VCOB-B750-4L-40-TA-MDL03-682/682M

682/682M NEEDS TO BE DETERMINED BASED ON EXISTING FITTER SEE RETROFIT FITTER DETAILS.

NOTE IF FIXTURES THAT WERE GUTTED AND CONVERTED TO INDUCTION LAMPS WOULD HAVE TO BE EVALUATED TO MAKE SURE THEY WOULD STILL WORK WITH THIS CONVERSION KIT.

Representative Contact – PLPSoCal

Crissy Cosci – 626-482-8420

ccosci@plpsocal.com